## en_US
1 | 1 | 1 | Cell UV Alarm | Min Voltage ID,U16,1,0, | Min Voltage,U16,0.0001,0,V | Voltage Threshold,U16,0.0001,0,V
2 | 1 | 2 | Cell UV Fault | Min Voltage ID,U16,1,0, | Min Voltage,U16,0.0001,0,V | Voltage Threshold,U16,0.0001,0,V
3 | 1 | 3 | Cell OV Alarm | Max Voltage ID,U16,1,0, | Max Voltage,U16,0.0001,0,V | Voltage Threshold,U16,0.0001,0,V
4 | 1 | 4 | Cell OV Fault | Max Voltage ID,U16,1,0, | Max Voltage,U16,0.0001,0,V | Voltage Threshold,U16,0.0001,0,V
5 | 1 | 5 | Cell DIff Alarm | Max /Min Voltage ID,U16,1,0, | Voltage DIff,U16,0.0001,0,V | Voltage Threshold,U16,0.0001,0,V
6 | 1 | 6 | Cell DIff Fault | Max /Min Voltage ID,U16,1,0, | Voltage DIff,U16,0.0001,0,V | Voltage Threshold,U16,0.0001,0,V
7 | 1 | 7 | Cell Voltage Wire-Open Alarm | Wire-Open ID,U16,1,0, | Cell Voltage,U16,0.0001,0,V
8 | 1 | 8 | Cell Fault Reversion | Cell ID,U16,1,0, | Cell Voltage,U16,0.0001,0,V
9 | 1 | 9 | Module OT Alarm | Max Temperature ID,U16,1,0, | Max Temperature,I16,0.1,0,℃ | Temperature Threshold,I16,0.1,0,℃
10 | 1 | 10 | Module OT Fault | Max Temperature ID,U16,1,0, | Max Temperature,I16,0.1,0,℃ | Temperature Threshold,I16,0.1,0,℃
11 | 1 | 11 | Module UT Alarm | Min Temperature ID,U16,1,0, | Min Temperature,I16,0.1,0,℃
12 | 1 | 12 | Module UT Fault | Min Temperature ID,U16,1,0, | Min Temperature,I16,0.1,0,℃
13 | 1 | 13 | Module Temperature Diff Alarm | Max/Min Temperature ID,U16,1,0, | Temperature Diff,I16,0.1,0,℃
14 | 1 | 14 | Module Temperature Diff Fault | Max/Min Temperature ID,U16,1,0, | Temperature Diff,I16,0.1,0,℃
15 | 1 | 15 | Module Temperature Rise Alarm | Max Temperature Rise ID,U16,1,0, | Max Temperature Rise,I16,0.1,0,℃
16 | 1 | 16 | Module Temperature Rise Fault | Max Temperature Rise ID,U16,1,0, | Max Temperature Rise,I16,0.1,0,℃
17 | 1 | 17 | Module Temperature Wire-Open Alarm | Module Temperature Wire-Open ID,U16,1,0, | Module Temperature,I16,0.1,0,℃
18 | 1 | 18 | Module Temperature Reversion | Module Temperature ID,U16,1,0, | Module Temperature,I16,0.1,0,℃
19 | 1 | 19 | Pole OT Alarm | Max Pole Temperature ID,U16,1,0, | Max Pole Temperature,I16,0.1,0,℃
20 | 1 | 20 | Pole OT Fault | Max Pole Temperature ID,U16,1,0, | Max Pole Temperature,I16,0.1,0,℃
21 | 1 | 21 | Pole Fault Reversion | Pole Temperature ID,U16,1,0, | Pole Temperature,I16,0.1,0,℃
22 | 1 | 22 | OC Alarm |  | Current,I16,0.1,0,A
23 | 1 | 23 | OC Fault |  | Current,I16,0.1,0,A
24 | 1 | 24 | OC Reversion |  | Current,I16,0.1,0,A
25 | 1 | 25 | Short-Circuit Fault |  | Current,I16,0.1,0,A
26 | 1 | 26 | String OV Alarm |  | String Voltage,U16,0.1,0,V
27 | 1 | 27 | String OV Fault |  | String Voltage,U16,0.1,0,V
28 | 1 | 28 | String UV Alarm |  | String Voltage,U16,0.1,0,V
29 | 1 | 29 | String UV Fault |  | String Voltage,U16,0.1,0,V
30 | 1 | 30 | String Fault Reversion |  | String Voltage,U16,0.1,0,V
31 | 1 | 31 | String INS Fault |  | INS RES,U16,1,0,kΩ
32 | 1 | 32 | String INS Fault Reversion |  | INS RES,U16,1,0,kΩ
33 | 1 | 33 | String leakage Current Fault |  | leakage Current,U16,1,0,mA
34 | 1 | 34 | String leakage Current Fault Reversion |  | leakage Current,U16,1,0,mA
35 | 1 | 35 | Begin CHG | SOC,U16,1,0,% | Current,I16,0.1,0,A
36 | 1 | 36 | Stop CHG | SOC,U16,1,0,% | System status,U16,1,0,
37 | 1 | 37 | Begin DSG | SOC,U16,1,0,% | Current,I16,0.1,0,A
38 | 1 | 38 | Stop DSG | SOC,U16,1,0,% | System status,U16,1,0,
39 | 1 | 39 | Battery Fully-CHG | SOC,U16,1,0,% | System status,U16,1,0,
40 | 1 | 40 | Battery Empty-DSG | SOC,U16,1,0,% | System status,U16,1,0,
41 | 1 | 41 | Balance Start | Balance ID,U16,1,0, | Balance status,U16,1,0,
42 | 1 | 42 | Balance Stop | Balance ID,U16,1,0, | Balance status,U16,1,0,
43 | 1 | 43 | QF Switch Off |  | QF status,U16,1,0,
44 | 1 | 44 | KM+ Switch Off |  | KM+ status,U16,1,0,
45 | 1 | 45 | KM- Switch Off |  | KM- status,U16,1,0,
46 | 1 | 46 | KM+ Switch On |  | KM+ status,U16,1,0,
47 | 1 | 47 | KM- Switch On |  | KM- status,U16,1,0,
48 | 1 | 48 | Fan Turn On |  | Fan status,U16,1,0,
49 | 1 | 49 | Fan Turn Off |  | Fan status,U16,1,0,
50 | 1 | 50 | BMS Start Running
51 | 1 | 51 | Configuration Change | Configuration Para ID,U16,1,0, | Configuration,U16,1,0,
52 | 1 | 52 | CMU Upgrade Verify Failed
53 | 1 | 53 | CMU Upgrade Successed |  | CMU Version,U16,1,0,
54 | 1 | 54 | CMU Upgrade Download Failed |  | Fault Code,U16,1,0,
55 | 1 | 55 | BMU Upgrade
56 | 1 | 56 | BMU Upgrade Successed |  | BMUVersion ,U16,1,0,
57 | 1 | 57 | BMU Upgrade Failed |  | Fault Code ,U16,1,0,
58 | 1 | 58 | BMU Disconnected | Disconnected BMU ID,U16,1,0,
59 | 1 | 59 | CCU Comm Fault
60 | 1 | 60 | RTU Comm Fault
61 | 1 | 61 | Cell Voltage Wire-Open Reversion
62 | 1 | 62 | Temperature Wire-Open Reversion
63 | 1 | 63 | String Pole OT Protection |  | Max Pole Temperature,U16,1,0,℃
64 | 1 | 64 | String Pole OT Alarm |  | Max Pole Temperature,U16,1,0,℃
65 | 1 | 65 | String Pole Wire-Open Alarm |  | Temperature Wire-Open status,U16,1,0,
66 | 1 | 66 | String Pole Reversion |  | Module Min /Max Temperature,U16,1,0,℃
67 | 1 | 67 | QF Fault (Non-Act) |  | Breaker Status Check,U16,1,0,
68 | 1 | 68 | KM Fault (Non-Act) |  | Conductor Status Check,U16,1,0,
69 | 1 | 69 | KMR Action | coil ID,U16,1,0, | KMR Status Check status,U16,1,0,
70 | 1 | 128 | Smoke Sensor Action |  | DI status Check,U16,1,0,
71 | 1 | 129 | Water Immersion Action |  | DI status Check,U16,1,0,
72 | 1 | 130 | Fire Action |  | DI status Check,U16,1,0,
73 | 1 | 131 | Emergency Stop Action |  | DI status CheckU16,1,0,
74 | 2 | 1 | Cell UV Alarm | Min Voltage ID,U16,1,0, | Min Voltage,U16,0.0001,0,V | Voltage Threshold,U16,0.0001,0,V
75 | 2 | 2 | Cell UV Fault | Min Voltage ID,U16,1,0, | Min Voltage,U16,0.0001,0,V | Voltage Threshold,U16,0.0001,0,V
76 | 2 | 3 | Cell OV Alarm | Max Voltage ID,U16,1,0, | Max Voltage,U16,0.0001,0,V | Voltage Threshold,U16,0.0001,0,V
77 | 2 | 4 | Cell OV Fault | Max Voltage ID,U16,1,0, | Max Voltage,U16,0.0001,0,V | Voltage Threshold,U16,0.0001,0,V
78 | 2 | 5 | Cell DIff Alarm (Reserved)
79 | 2 | 6 | Cell DIff Fault (Reserved)
80 | 2 | 7 | Cell Voltage Wire-Open Alarm | Wire-Open BMU ID,U16,1,0, |  | Voltage Wire-Open status,BIN,1,0,
81 | 2 | 8 | Cell Fault Reversion |  | Cell Max Voltage,U16,0.0001,0,V | Min Voltage,U16,0.0001,0,V
82 | 2 | 9 | Module OT Alarm | Max Temperature ID,U16,1,0, | Max Temperature,I16,0.1,0,℃ | Temperature Threshold,I16,0.1,0,℃
83 | 2 | 10 | Module OT Fault | Max Temperature ID,U16,1,0, | Max Temperature,I16,0.1,0,℃ | Temperature Threshold,I16,0.1,0,℃
84 | 2 | 11 | Module UT Alarm | Min Temperature ID,U16,1,0, | Min Temperature,I16,0.1,0,℃ | Temperature Threshold,I16,0.1,0,℃
85 | 2 | 12 | Module UT Fault | Min Temperature ID,U16,1,0, | Min Temperature,I16,0.1,0,℃ | Temperature Threshold,I16,0.1,0,℃
86 | 2 | 13 | Module Temperature Diff Alarm (Reserved)
87 | 2 | 14 | Module Temperature Diff Fault (Reserved)
88 | 2 | 15 | Module Temperature Rise Alarm (Reserved)
89 | 2 | 16 | Module Temperature Rise Fault (Reserved)
90 | 2 | 17 | Module Temperature Wire-Open Alarm | Wire-Open BMU,U16,1,0, |  | Temperature Wire-Open status,BIN,1,0,
91 | 2 | 18 | Module Temperature Reversion |  | Module Max,I16,0.1,0,℃ | Min Temperature,I16,0.1,0,℃
92 | 2 | 19 | Pole OT Alarm | Max Pole Temperature ID,U16,1,0, | Max Pole Temperature,I16,0.1,0,℃ | Temperature Threshold,I16,0.1,0,℃
93 | 2 | 20 | Pole OT Fault | Max Pole Temperature ID,U16,1,0, | Max Pole Temperature,I16,0.1,0,℃ | Temperature Threshold,I16,0.1,0,℃
94 | 2 | 21 | Pole Fault Reversion |  | Pole Max Temperature,I16,0.1,0,℃ | Temperature Threshold,I16,0.1,0,℃
95 | 2 | 22 | OC Alarm |  | Current,I16,0.1,0,A | Current Threshold,I16,0.1,0,A
96 | 2 | 23 | OC Fault |  | Current,I16,0.1,0,A | Current Threshold,I16,0.1,0,A
97 | 2 | 24 | OC Reversion |  | Current,I16,0.1,0,A | Current Threshold,I16,0.1,0,A
98 | 2 | 25 | Short-Circuit Fault |  | Current,I16,0.1,0,A | Current Threshold,I16,0.1,0,A
99 | 2 | 26 | String OV Alarm |  | String Voltage,U16,0.1,0,V | String Voltage Threshold,U16,0.1,0,V
100 | 2 | 27 | String OV Fault |  | String Voltage,U16,0.1,0,V | String Voltage Threshold,U16,0.1,0,V
101 | 2 | 28 | String UV Alarm |  | String Voltage,U16,0.1,0,V | String Voltage Threshold,U16,0.1,0,V
102 | 2 | 29 | String UV Fault |  | String Voltage,U16,0.1,0,V | String Voltage Threshold,U16,0.1,0,V
103 | 2 | 30 | String Fault Reversion |  | String Voltage,U16,0.1,0,V | String Voltage Threshold,U16,0.1,0,V
104 | 2 | 31 | String INS Fault |  | INS RES,U16,0.1,0,kΩ | INS RES Threshold,U16,0.1,0,kΩ
105 | 2 | 32 | String INS Fault Reversion |  | INS RES,U16,0.1,0,kΩ | INS RES Threshold,U16,0.1,0,kΩ
106 | 2 | 33 | String leakage Current Fault |  | leakage Current,I16,0.1,0,mA | leakage Current Threshold,I16,0.1,0,mA
107 | 2 | 34 | String leakage Current Fault Reversion |  | leakage Current,I16,0.1,0,mA | leakage Current Threshold,I16,0.1,0,mA
108 | 2 | 35 | Begin CHG | Last-Time System status,MAP | String Current,I16,0.1,0,A | CHG/DSG Current Detect Threshold,I16,0.1,0,A | {"evt_id":{"2":" DSG ","4":"Stop"}}
109 | 2 | 36 | Stop CHG | Last-Time System status,MAP | String Current,I16,0.1,0,A |  | {evt_id:{1: CHG }}
110 | 2 | 37 | Begin DSG | Last-Time System status,MAP | String Current,I16,0.1,0,A | CHG/DSG Current Detect Threshold,I16,0.1,0,A | {"evt_id":{"1":" CHG ","4":"Stop"}}
111 | 2 | 38 | Stop DSG | Last-Time System status,MAP | String Current,I16,0.1,0,A |  | {evt_id:{2: DSG }}
112 | 2 | 39 | Battery Fully-CHG | Max Voltage ID,U16,1,0, | String Voltage,U16,0.1,0,V | Max Cell Voltage,U16,0.0001,0,V
113 | 2 | 40 | Battery Empty-DSG | Min Voltage ID,U16,1,0, | String Voltage,U16,0.1,0,V | Min Cell Voltage,U16,0.0001,0,V
114 | 2 | 41 | Balance Start (Reserved)
115 | 2 | 42 | Balance Stop (Reserved)
116 | 2 | 43 | QF Switch Off | coil ID,U16,1,0, |  | QF Relay status,MAP | {"evt_threshold":{"0":"Off","1":"On"}}
117 | 2 | 44 | KM+ Switch Off | coil ID,U16,1,0, |  | KM+ Relay status,MAP | {"evt_threshold":{"0":"Off","1":"On"}}
118 | 2 | 45 | KM- Switch Off | coil ID,U16,1,0, |  | KM- Relay status,MAP | {"evt_threshold":{"0":"Off","1":"On"}}
119 | 2 | 46 | KM+ Switch On | coil ID,U16,1,0, |  | KM+ Relay status,MAP | {"evt_threshold":{"0":"Off","1":"On"}}
120 | 2 | 47 | KM- Switch On | coil ID,U16,1,0, |  | KM- Relay status,MAP | {"evt_threshold":{"0":"Off","1":"On"}}
121 | 2 | 48 | Fan Turn On | Fan Relay status | Max Battery Temperature,I16,0.1,0,℃ | Environmental Control Temperature Threshold,I16,0.1,0,℃
122 | 2 | 49 | Fan Turn Off | Fan Relay status | Max Battery Temperature,I16,0.1,0,℃ | Environmental Control Temperature Threshold,I16,0.1,0,℃
123 | 2 | 50 | BMS Start | Start Register,U16,1,0,
124 | 2 | 51 | Configuration Change | Configuration Para ID,MAP,1,5358, | Configuration Before Changed,U16,1,0, | Configuration After Changed,U16,1,0, | {"evt_id":{"5358":"Precharge Stop Time","5359":"Precharge Stop Current ","5360":"Reserved Sensor Range","5361":"String Battery Rated capacity","5362":"Min Detection Current","5363":"String Battery Fully-CHG Hysteresis","5364":"String Battery Empty-DSG Hysteresis","5365":"Environmental Control Temperature Hysteresis","5366":"Temp Ambient Upper Limit","5367":"Temp Ambient Lower Limit","5368":"String Battery SOC Upper Limit","5369":"String Battery SOC Lower Limit","5370":"String Pole OT Alarm ","5371":"String Pole OT Fault","5372":"String Battery INS RES Alarm","5373":"String Battery leakage Current Alarm","5374":"Cell DIff Alarm","5375":"Cell DIff Fault","5376":"Cell OV Alarm","5377":"Cell OV Falut","5378":"Cell UV Alarm","5379":"Cell UV Fault","5380":"Cell OT Alarm","5381":"Cell OT Fault","5382":"Cell UT Alarm","5383":"Cell UT Fault","5384":"Cell Temperature Diff Alarm ","5385":"Cell Temperature Diff Fault","5386":"Cell Temperature Rise Alarm ","5387":"Cell Temperature Rise Fault","5388":"PackPole OT Alarm","5389":"PackPole OT Fault","5390":"CHG/DSG OC Alarm","5391":"CHG/DSG OC Fault","5392":"Short-Circuit Current Fault","5393":"String OV Alarm","5394":"String OV Fault","5395":"String UV Alarm","5396":"String UV Fault","5397":"String Battery INS RES Fault","5398":"String Battery leakage Current Fault","5399":"Alarm Delay","5400":"Protection Delay","5401":"String Battery Capacity","5402":"String Battery Calibrated Capacity","5403":"String Battery Remain Power","5404":"CHG/DSG Rated Current ","5405":"Current Sensor Range","5406":"leakage Current Sensor Range","5407":"Voltage Sensor Range","5408":"Battery Balance Mode","5409":"Balance Config/Threshold","5410":"Balance Start Voltage Diff","5411":"Num of String Packs","5412":"Num of BMU Cell Volt","5413":"Num of BMU Cell Temperature ","5414":"Num of BMU Pole Temperature","5415":"nBC Alarm Masking Bits","5416":"nBC Fault Masking Bits","5417":"CMU Function Enable Bits 1 ","5418":"IP Addr Lower Byte","5419":"IP Addr Higher Byte ","5420":"NTP Server Addr Lower Byte","5421":"NTP Server Addr Higher Byte","5422":"Data Masking Bits 1","5423":"Data Masking Bit 2","5424":"Data Masking Bits 3","5425":"Data Masking Bits 4","5426":"System Fault Masking Bits 1","5427":"System Fault Masking Bits 2","5428":"System Alarm Masking Bits 1","5429":"System Alarm Masking Bits 2","5430":"CMU Function Enable Bits 2","5431":"Fully-CHG/Empty-DSG String Voltage Hysteresis","5432":"Cell Voltage Data Masking Bits","5433":"Temperature Data Masking Bits"}}
125 | 2 | 52 | CMU Upgrade Verify Failed
126 | 2 | 53 | CMU Upgrade Successed
127 | 2 | 54 | CMU Upgrade Download Failed
128 | 2 | 55 | BMU Fault | Fault BMU ID,U16,1,0, |  | Fault status,BIN,1,0,
129 | 2 | 56 | Remote IO Control(Modbus) | ,MAP | Remote IP,U16,1,0, | ,MAP | {"evt_id":{"0":"KM+","1":"KM-","2":"KMR","3":"QF","4":"Integrated Cmd"},"evt_threshold":{"43605":" Switch On ","21930":" Switch Off "}}
130 | 2 | 57 | External Hardware QF Tripping Action
131 | 2 | 58 | System AC Power Down
132 | 2 | 59 | BMU Fault Reversion | Reversion BMU ID,U16,1,0,
133 | 2 | 60 | Precharge Failed |  | Current ,I16,0.1,0,A | Precharge Current Limit Value,I16,0.1,0,A
134 | 2 | 61 | Cell Voltage Wire-Open Reversion | Reversion BMU ID,U16,1,0,
135 | 2 | 62 | Temperature Wire-Open Reversion | Reversion BMU ID,U16,1,0,
136 | 2 | 63 | String Pole OT Protection | Max Pole Temperature ID,U16,1,0, | Max Pole Temperature,I16,0.1,0,℃ | Temperature Threshold,I16,0.1,0,℃
137 | 2 | 64 | String Pole OT Alarm | Max Pole Temperature ID,U16,1,0, | Max Pole Temperature,I16,0.1,0,℃ | Temperature Threshold,I16,0.1,0,℃
138 | 2 | 65 | String Pole Wire-Open Alarm |  |  | Temperature Wire-Open status,BIN,1,0,
139 | 2 | 66 | String Pole Fault Reversion |  | Max Pole Temperature,I16,0.1,0,℃ | Temperature Threshold,I16,0.1,0,℃
140 | 2 | 67 | Reserved
141 | 2 | 68 | KM Fault (Non-Act) | DI status,U16,1,0, |  | DO status,U16,1,0,
142 | 2 | 69 | KMR Action | coil ID,U16,1,0, |  | KMR Relay status,MAP | {"evt_threshold":{"0":"Off","1":"On"}}
143 | 2 | 70 | UV Self-Proteced | Min Cell Voltage ID,U16,1,0, | Min Cell Voltage,U16,0.0001,0,V | Self-Proteced Threshold,U16,0.0001,0,V
144 | 2 | 71 | QF status Change | Status Before Changed,MAP |  | Status After Changed,MAP | {"evt_id":{"0":"Off","1":"On"},"evt_threshold":{"0":"Off","1":"On"}}
145 | 2 | 72 | KM+ status Change | Status Before Changed,MAP |  | Status After Changed,MAP | {"evt_id":{"0":"Off","1":"On"},"evt_threshold":{"0":"Off","1":"On"}}
146 | 2 | 73 | KM- status Change | Status Before Changed,MAP |  | Status After Changed,MAP | {"evt_id":{"0":"Off","1":"On"},"evt_threshold":{"0":"Off","1":"On"}}
147 | 2 | 74 | KMR status Change | Status Before Changed,MAP |  | Status After Changed,MAP | {"evt_id":{"0":"Off","1":"On"},"evt_threshold":{"0":"Off","1":"On"}}
148 | 2 | 128 | Smoke Sensor Action |  |  | DI status Check,BIN,1,0,
149 | 2 | 129 | Water Immersion Action |  |  | DI status Check,BIN,1,0,
150 | 2 | 130 | Fire Action |  |  | DI status Check,BIN,1,0,
151 | 2 | 131 | Emergency Stop Action |  |  | DI status Check,BIN,1,0,
152 | 2 | 75 | Balance Fault | BMU ID,U16,1,0, | Fault status,U16,1,0, | Fault status,U16,1,0,
153 | 2 | 76 | EEPROM Error
154 | 2 | 77 | Parameters Reset To Default
155 | 2 | 78 | INS Fault BUS Voltage |  | PE-B+ Voltage,U16,0.1,0,V | PE-B- Voltage,U16,0.1,0,V
156 | 2 | 79 | Reserved Current SensorWire-Open |  |  | Two Current Sensor Difference,U16,1,0,A
157 | 2 | 80 | RTC Read Failed
158 | 2 | 81 | System Para Read Failed | Type,MAP |  |  | {"evt_id":{"1":"Initial","2":"Power","3":"Calibration","4":"SOC Table"}}
159 | 2 | 82 | BMU DIP-Switch Error | Error Code,U16,1,0, |  | BMU ID,U16,1,0,
160 | 2 | 83 | MODBUS Data Error | Cmd,U16,1,0, | Addr,U16,1,0, | Len,U16,1,0,
161 | 2 | 84 | BMU Upgrade |  |  | Result,MAP | {"evt_threshold":{"0":"Successed ","1":"Failed "}}
162 | 2 | 85 | INS Upgrade |  | Result,MAP |  | {"evt_dt":{"0":"Failed ","1":"Successed "}}
163 | 2 | 86 | Load Fault Wave Record |  |  | Error Code,U16,1,0,
164 | 2 | 87 | CHG SOC Abnormal |  | Remain Power,U16,0.1,0,kWh | After Calibration Rated Capacity,U16,0.1,0,kWh
165 | 2 | 88 | Balance Compensate Begin | Voltage,U16,0.0001,0,V | Target Voltage,U16,0.0001,0,V
166 | 2 | 89 | Balance Compensate Stop | Voltage,U16,0.0001,0,V | Target Voltage,U16,0.0001,0,V
167 | 3 | 1 | Cell UV Alarm | Min Voltage ID,U16,1,0, | Min Voltage,U16,0.0001,0,V | Voltage Threshold,U16,0.0001,0,V
168 | 3 | 2 | Cell UV Fault | Min Voltage ID,U16,1,0, | Min Voltage,U16,0.0001,0,V | Voltage Threshold,U16,0.0001,0,V
169 | 3 | 3 | Cell OV Alarm | Max Voltage ID,U16,1,0, | Max Voltage,U16,0.0001,0,V | Voltage Threshold,U16,0.0001,0,V
170 | 3 | 4 | Cell OV Fault | Max Voltage ID,U16,1,0, | Max Voltage,U16,0.0001,0,V | Voltage Threshold,U16,0.0001,0,V
171 | 3 | 5 | Cell Voltage Diff Alarm (Reserved)
172 | 3 | 6 | Cell Voltage Diff Fault (Reserved)
173 | 3 | 7 | Cell Voltage Wire-Open Alarm | Wire-Open BMU ID,U16,1,0, |  | Voltage Wire-Open status,BIN,1,0,
174 | 3 | 8 | Cell Fault Reversion |  | Cell Max Voltage,U16,0.0001,0,V | Min Voltage,U16,0.0001,0,V
175 | 3 | 9 | Module OT Alarm | Max Temperature ID,U16,1,0, | Max Temperature,I16,0.1,0,℃ | Temperature Threshold,I16,0.1,0,℃
176 | 3 | 10 | Module OT Fault | Max Temperature ID,U16,1,0, | Max Temperature,I16,0.1,0,℃ | Temperature Threshold,I16,0.1,0,℃
177 | 3 | 11 | Module UT Alarm | Min Temperature ID,U16,1,0, | Min Temperature,I16,0.1,0,℃ | Temperature Threshold,I16,0.1,0,℃
178 | 3 | 12 | Module UT Fault | Min Temperature ID,U16,1,0, | Min Temperature,I16,0.1,0,℃ | Temperature Threshold,I16,0.1,0,℃
179 | 3 | 13 | Module Temperature Diff Alarm (Reserved)
180 | 3 | 14 | Module Temperature Diff Fault (Reserved)
181 | 3 | 15 | Module Temperature Rise Alarm (Reserved)
182 | 3 | 16 | Module Temperature Rise Fault (Reserved)
183 | 3 | 17 | Module Temperature Wire-Open Alarm | Wire-Open BMU,U16,1,0, |  | Temperature Wire-Open status,BIN,1,0,
184 | 3 | 18 | Module Temperature Reversion |  | Module Max,I16,0.1,0,℃ | Min Temperature,I16,0.1,0,℃
185 | 3 | 19 | Pole OT Alarm | Max Pole Temperature ID,U16,1,0, | Max Pole Temperature,I16,0.1,0,℃ | Temperature Threshold,I16,0.1,0,℃
186 | 3 | 20 | Pole OT Fault | Max Pole Temperature ID,U16,1,0, | Max Pole Temperature,I16,0.1,0,℃ | Temperature Threshold,I16,0.1,0,℃
187 | 3 | 21 | Pole Fault Reversion |  | Pole Max Temperature,I16,0.1,0,℃ | Temperature Threshold,I16,0.1,0,℃
188 | 3 | 22 | OC Alarm |  | Current,I16,0.1,0,A | Current Threshold,I16,0.1,0,A
189 | 3 | 23 | OC Fault |  | Current,I16,0.1,0,A | Current Threshold,I16,0.1,0,A
190 | 3 | 24 | OC Reversion |  | Current,I16,0.1,0,A | Current Threshold,I16,0.1,0,A
191 | 3 | 25 | Short-Circuit Fault |  | Current,I16,0.1,0,A | Current Threshold,I16,0.1,0,A
192 | 3 | 26 | String OV Alarm |  | String Voltage,U16,0.1,0,V | String Voltage Threshold,U16,0.1,0,V
193 | 3 | 27 | String OV Fault |  | String Voltage,U16,0.1,0,V | String Voltage Threshold,U16,0.1,0,V
194 | 3 | 28 | String UV Alarm |  | String Voltage,U16,0.1,0,V | String Voltage Threshold,U16,0.1,0,V
195 | 3 | 29 | String UV Fault |  | String Voltage,U16,0.1,0,V | String Voltage Threshold,U16,0.1,0,V
196 | 3 | 30 | String Fault Reversion |  | String Voltage,U16,0.1,0,V | String Voltage Threshold,U16,0.1,0,V
197 | 3 | 31 | String INS Fault |  | INS RES,U16,0.1,0,kΩ | INS RES Threshold,U16,0.1,0,kΩ
198 | 3 | 32 | String INS Fault Reversion |  | INS RES,U16,0.1,0,kΩ | INS RES Threshold,U16,0.1,0,kΩ
199 | 3 | 33 | String leakage Current Fault |  | leakage Current,I16,0.1,0,mA | leakage Current Threshold,I16,0.1,0,mA
200 | 3 | 34 | String leakage Current Fault Reversion |  | leakage Current,I16,0.1,0,mA | leakage Current Threshold,I16,0.1,0,mA
201 | 3 | 35 | Begin CHG | Last-Time System status,MAP | String Current,I16,0.1,0,A | CHG/DSG Current Detect Threshold,I16,0.1,0,A | {"evt_id":{"2":" DSG ","4":"Stop"}}
202 | 3 | 36 | Stop CHG | Last-Time System status,MAP | String Current,I16,0.1,0,A |  | {evt_id:{1: CHG }}
203 | 3 | 37 | Begin DSG | Last-Time System status,MAP | String Current,I16,0.1,0,A | CHG/DSG Current Detect Threshold,I16,0.1,0,A | {"evt_id":{"1":" CHG ","4":"Stop"}}
204 | 3 | 38 | Stop DSG | Last-Time System status,MAP | String Current,I16,0.1,0,A |  | {evt_id:{2: DSG }}
205 | 3 | 39 | Battery Fully-CHG | Max Voltage ID,U16,1,0, | String Voltage,U16,0.1,0,V | Max Cell Voltage,U16,0.0001,0,V
206 | 3 | 40 | Battery Empty-DSG | Min Voltage ID,U16,1,0, | String Voltage,U16,0.1,0,V | Min Cell Voltage,U16,0.0001,0,V
207 | 3 | 41 | Balance Start (Reserved)
208 | 3 | 42 | Balance Stop (Reserved)
209 | 3 | 43 | QF Switch Off | coil ID,U16,1,0, |  | QF Relay status,MAP | {"evt_threshold":{"0":"Off","1":"On"}}
210 | 3 | 44 | KM+ Switch Off | coil ID,U16,1,0, |  | KM+ Relay status,MAP | {"evt_threshold":{"0":"Off","1":"On"}}
211 | 3 | 45 | KM- Switch Off | coil ID,U16,1,0, |  | KM- Relay status,MAP | {"evt_threshold":{"0":"Off","1":"On"}}
212 | 3 | 46 | KM+ Switch On | coil ID,U16,1,0, |  | KM+ Relay status,MAP | {"evt_threshold":{"0":"Off","1":"On"}}
213 | 3 | 47 | KM- Switch On | coil ID,U16,1,0, |  | KM- Relay status,MAP | {"evt_threshold":{"0":"Off","1":"On"}}
214 | 3 | 48 | Fan Turn On | Fan Relay status | Max Battery Temperature,I16,0.1,0,℃ | Environmental Control Temperature Threshold,I16,0.1,0,℃
215 | 3 | 49 | Fan Turn Off | Fan Relay status | Max Battery Temperature,I16,0.1,0,℃ | Environmental Control Temperature Threshold,I16,0.1,0,℃
216 | 3 | 50 | BMS Start | Start Register,U16,1,0,
217 | 3 | 51 | Configuration Change | Configuration Para,MAP,1,5358, | Configuration Before Changed,U16,1,0, | Configuration After Changed,U16,1,0, | {"evt_id":{"5358":"Precharge Stop Time","5359":"Precharge Stop Current","5360":"Reserved Sensor Range","5361":"String Battery Rated Capacity","5362":"CHG/DSG Current Min Detection Current","5363":"String Battery Fully-CHG Hysteresis","5364":"String Battery Empty-DSG Hysteresis","5365":"Environmental Control Temperature Hysteresis","5366":"Temp Ambient Upper Limit","5367":"Temp Ambient Lower Limit","5368":"String Battery SOC Upper Limit","5369":"String Battery SOC Lower Limit","5370":"String Pole OT Alarm ","5371":"String Pole OT Fault","5372":"String Battery INS RES Alarm","5373":"String Battery leakage Current Alarm","5374":"Cell DIff Alarm","5375":"Cell DIff Fault","5376":"Cell OV Alarm ","5377":"Cell OV Fault","5378":"Cell UV Alarm","5379":"Cell UV Fault","5380":"Cell OV Alarm","5381":"Cell UV Fault","5382":"Cell UV Alarm","5383":"Cell UV Fault","5384":"Cell Temperature Diff Alarm","5385":"Cell Temperature Diff Fault","5386":"Cell Temperature Rise Alarm","5387":"Cell Temperature Rise Fault","5388":"PackPole OT Alarm","5389":"PackPole OT Fault","5390":"CHG/DSG OC Alarm","5391":""CHG/DSG OC Fault","5392":"Short-Circuit Current Fault","5393":"String OV Alarm","5394":"String OV Fault","5395":"String UV Alarm","5396":"String UV Fault","5397":"String Battery INS RES Fault","5398":"String Battery leakage Current Fault","5399":"Alarm Delay","5400":"Fault Delay","5401":"String Battery Capacity","5402":"String Battery Calibration Rated Capacity","5403":"String Battery Remain Power","5404":"CHG/ DSG Rated Current ","5405":"Current Sensor Range","5406":"leakage Current Sensor Range","5407":"Voltage Sensor Range","5408":"Battery Balance Mode","5409":"Balance Config/Threshold","5410":"Balance Target Voltage ","5411":"Num of String Packs","5412":"Num of Pack Cell Voltage","5413":"Num of Pack Cell Temperature","5414":"Num of Pack Pole Temperature","5415":"nBC Alarm Masking Bits","5416":"nBCFault Masking Bits","5417":"CMU Function Enable Bits 1","5418":"IP Addr Lower Bytes","5419":"IP Addr Higher Bytes ","5420":"NTP Server Addr Lower Byte","5421":"NTP Server Addr Higher Bytes","5422":"Data Masking Bits 1","5423":"Data Masking Bits 2","5424":"Data Masking Bits 3","5425":"Data Masking Bits 4","5426":"System Fault Masking Register 1","5427":"System Fault Masking Register 2","5428":"System Alarm Masking Register 1","5429":"System Alarm Masking Register 2","5430":"CMU Function Enable Bits 2","5431":"Fully-CHGEmpty-DSGString Voltage Hysteresis","5432":"Cell Voltage Data Masking Bits","5433":"Temperature Data Masking Bits","5434":"Balance Start Voltage Diff"}}
218 | 3 | 52 | CMU Upgrade Verify Failed
219 | 3 | 53 | CMU Upgrade Successed
220 | 3 | 54 | CMU Upgrade Download Failed
221 | 3 | 55 | BMU Fault | Fault BMU ID,U16,1,0, |  | Fault status,BIN,1,0,
222 | 3 | 56 | Remote IO Control(Modbus) | ,MAP | Remote IP,U16,1,0, | ,MAP | {"evt_id":{"0":"KM+","1":"KM-","2":"KMR","3":"QF","4":"Integrated Cmd"},"evt_threshold":{"43605":" Switch On ","21930":" Switch Off "}}
223 | 3 | 57 | External Hardware QF Tripping Action
224 | 3 | 58 | System AC Power Down
225 | 3 | 59 | BMU Fault Reversion | Reversion BMU ID,U16,1,0,
226 | 3 | 60 | Precharge Failed |  | Current,I16,0.1,0,A | Precharge Current Limit Value,I16,0.1,0,A
227 | 3 | 61 | Cell Voltage Wire-Open Reversion | Reversion BMU ID,U16,1,0,
228 | 3 | 62 | Temperature Wire-Open Reversion | Reversion BMU ID,U16,1,0,
229 | 3 | 63 | String Pole OT Protection | Max Pole Temperature ID,U16,1,0, | Max Pole Temperature,I16,0.1,0,℃ | Temperature Threshold,I16,0.1,0,℃
230 | 3 | 64 | String Pole OT Alarm | Max Pole Temperature ID,U16,1,0, | Max Pole Temperature,I16,0.1,0,℃ | Temperature Threshold,I16,0.1,0,℃
231 | 3 | 65 | String Pole Wire-Open Alarm |  |  | Temperature Wire-Open status,BIN,1,0,
232 | 3 | 66 | String Pole Fault Reversion |  | Max Pole Temperature,I16,0.1,0,℃ | Temperature Threshold,I16,0.1,0,℃
233 | 3 | 67 | Reserved
234 | 3 | 68 | KMFault (Non-Act) | DI status,U16,1,0, |  | DO status,U16,1,0,
235 | 3 | 69 | KMRAction | coil ID,U16,1,0, |  | KMR Relay status,MAP | {"evt_threshold":{"0":"Off","1":"On"}}
236 | 3 | 70 | UV Self-Proteced | Min Cell Voltage ID,U16,1,0, | Min Cell Voltage,U16,0.0001,0,V | Self-Proteced Threshold,U16,0.0001,0,V
237 | 3 | 71 | QF status Change | Status Before Changed,MAP |  | Status After Changed,MAP | {"evt_id":{"0":"Off","1":"On"},"evt_threshold":{"0":"Off","1":"On"}}
238 | 3 | 72 | KM+ status Change | Status Before Changed,MAP |  | Status After Changed,MAP | {"evt_id":{"0":"Off","1":"On"},"evt_threshold":{"0":"Off","1":"On"}}
239 | 3 | 73 | KM- status Change | Status Before Changed,MAP |  | Status After Changed,MAP | {"evt_id":{"0":"Off","1":"On"},"evt_threshold":{"0":"Off","1":"On"}}
240 | 3 | 74 | KMR status Change | Status Before Changed,MAP |  | Status After Changed,MAP | {"evt_id":{"0":"Off","1":"On"},"evt_threshold":{"0":"Off","1":"On"}}
241 | 3 | 128 | Smoke Sensor Action |  |  | DI status Check,BIN,1,0,
242 | 3 | 129 | Water Immersion Action |  |  | DI status Check,BIN,1,0,
243 | 3 | 130 | Fire Action |  |  | DI status Check,BIN,1,0,
244 | 3 | 131 | Emergency Stop Action |  |  | DI status Check,BIN,1,0,
245 | 3 | 75 | Balance Fault | BMU ID号,U16,1,0, | Fault status,U16,1,0, | Fault status,U16,1,0,
246 | 3 | 76 | EEPROM Error
247 | 3 | 77 | Parameters Reset To Default
248 | 3 | 78 | INS Fault BUS Voltage |  | BUS PE-B+ Voltage,U16,0.1,0,V | BUS PE-B- Voltage,U16,0.1,0,V
249 | 3 | 79 | ReservedCurrent SensorWire-Open |  | Two Current Sensor Difference,U16,1,0,A | Current Sensor Difference,U16,1,0,A
250 | 3 | 80 | RTC Read Failed
251 | 3 | 81 | System Para Read Failed | Type,MAP |  |  | {"evt_id":{"1":"Initial","2":"Power","3":"Calibration","4":"SOC Table"}}
252 | 3 | 82 | BMU DIP-Switch Error | Error Code,U16,1,0, |  | BMU ID,U16,1,0,
253 | 3 | 83 | MODBUS data Error | 命令,U16,1,0, | Addr,U16,1,0, | Len,U16,1,0,
254 | 3 | 84 | BMU Upgrade |  |  | Result,MAP | {"evt_threshold":{"0":"Successed ","1":"Failed "}}
255 | 3 | 85 | INS Upgrade |  | Result After Upgrade,U16,1,0,
256 | 3 | 86 | Load Fault Wave Record |  |  | Error Code,U16,1,0,
257 | 3 | 87 | CHG SOC Abnormal |  | Remain Power,U16,0.1,0,kWh | Rated Capcity After Calibration,U16,0.1,0,kWh
258 | 3 | 89 | OV Self-Proteced Breaker Off | Max Voltage ID,U16,1,0, | Max Voltage,U16,0.0001,0,V
259 | 3 | 90 | Temperature Jump | Temperature ID,U16,1,0, | Before Jump Temperature,I16,0.1,0,℃ | After Jump Temperature,U16,0.1,0,℃